## Slide 1: TASK 2 Modeling & Simulation Fall 2013 Workflow
web software to support decision making
in building retrofit projects
Workflow + Case Study: Building101 tools.eebhub.org | developer.eebhub.org

## Slide 2
4 Platform Tools with different analytical capabilities
designed to engage the owner throughout a building retrofit lifecycle
tools.eebhub.org
tools.eebhub.org/visitors
over 600 visits & 2,000 page views last month!

## Slide 3: Simulation Platform PEOPLE
building
owners
building
designers
building
auditors
building
analysts
USERS
DEVELOPERS
Inverse Modeling
Toolkit
Design Advisor
CoolVent
Urban Weather Generator
Portfolio Inverse Modeling
Benchmarking
Manufacturer Materials
Energy Audit Tool
iPad Audit Interface
Parametric Analysis
Toolkit
Retrofit Manager
integrates

## Slide 4
DATA FLOW
among
INPUTS to platform interface
RESULTS from simulation engine
platform
tools
KEY for DATA FLOW

## Slide 5: Simulation Platform DATA
utility data
weather
typical room
shape of building
3D geometry,
efficiency measures
INPUTS
Energy Use
Intensity
Benchmark
with EnergyStar,
CBECS, EIA, LEED
Systems
Benchmark
OUTPUTS
MEASURES >
based on climate/budget
1-5
5-15
30-50
40-50
General System
Components
Breakdown
SubSystems
Audit
Targeted SubSystem
Replacement
Investigation
Installation
Staging
EUI actual vs. simulated
Daylighting, Airflow,
& all EnergyPlus Files
Benchmarking
Issues
+ EUI actual
Systems
Issues
SubSystem
to refine

## Slide 6: Retrofit Analysis

## Slide 7: COMPREHENSIVE Inputs & Outputs
building shape
air tightness level
typical room on each facade
40-80 Low > High Cost Measures with Retrofit Staging Timeline
DAYSIM: Shade Schedule
Lighting Shade Schedule, Spatial Daylight Autonomy, Critical Point Illuminance, Occupancy Sensors
CONTAM airflow, EnergyPlus energy use (heating/cooling)
+ all files (.idf, .rad, .sql) for experts
ECM Categories: Lighting/Daylighting, Plug/Process, Occupant, Envelope, HVAC
+owner desired
energy conservation measures
Building Component Library
SUBSTANTIAL
+3D geometry
import

## Slide 8: COMPREHENSIVE Daylighting, Airflow, Energy
Daylight Data File by Orientation
Hourly Shade Operation Schedule
Hourly Lighting Power Fraction
(representative spaces
on each orientation)
Annual Zone Lighting Energy & Savings
Building Energy Performance with Integrated Daylighting Controls,
Airflow, and Contaminant Transport Impacts
Airflow Calculation
OpenStudio input file created

## Slide 9: Daysim Development
Penn State added photosensor control system modeling and other modeling features (electric lighting, advanced shading device operation, system calibration, etc.), to the original version of Daysim that was developed by NRC-Canada & Fraunhofer Institute.
DAYSIMps is downloadable from www.daysim.ning.com.
The EEB Hub funded Daysim enhancements and the development of standalone Daysim modules for implementation in other programs.
A new user interface is currently being developed using OpenStudio’s menu system to apply these enhancements in an updated (new) version of DAYSIMps.

## Slide 10: Daylight Energy Savings Calculations
Typical spaces are applied at the center of each façade.
Window specifications determine whether ribbon or punched windows are considered (by façade).
EPW weather data are applied to determine hourly sky conditions using Perez skies.
Shading devices are applied on an hourly basis to block direct sunlight.
  Blinds = 20% transmittance
  Fabric Shades = 5% transmittance

## Slide 11: Daylight Calculations
8 ft. and 10 ft. luminaire row spacings are applied.
Different daylight control zones are considered (1 row, 2 rows, 3 rows, etc.).
Critical points are placed four feet from the side walls near the interior edge of each daylight zone.
A 70/30 contribution is considered from the dimmed and non-dimmed zones at the critical point.
Dimming levels are determined for each layout.
Room power levels are calculated.
The configuration with the highest energy savings is applied.

## Slide 12: Daylight Output
Monthly electric lighting energy savings table/graph.
Electric lighting power levels at each hour of the year are applied in an EnergyPlus schedule for each perimeter zone.
A shading device schedule is produced for each façade (for EnergyPlus).
Option - Daylight Autonomy contour graphs and Spatial Daylight Automony (sDA300 lux,50%) can be computed for each space (below).
sDA300 lux,50% = 63.5%

## Slide 13: Why Airflow Modeling?
Airflow in buildings are either
  Intentional (supply/return flow, exhaust…)
  Unintentional (infiltration, zone-to-zone leakage…)
Both types play a role in transport phenomena
  Heating and cooling
  Contaminant transport
Internal unintentional transport typically not modeled, infiltration should be modeled

## Slide 14: Infiltration Modeling
Infiltration accounts for up to 25% of load
Modeling is typically very coarse
  Standards/guidelines
  Rules of thumb
Alternate approach: use CONTAM to compute infiltration based on building airtightness

## Slide 15: What is CONTAM?
General purpose multizone airflow simulation code
Often used for contaminant transport simulation
Uses an “element assembly” model of the building
Leakage paths, air handlers, and other components of the model are represented as logical elements

## Slide 16: Approach
Translate energy model into airflow model
Run CONTAM to compute infiltration
Process CONTAM outputs to create enhanced energy model
Programmed using the OpenStudio SDK

## Slide 17: Automatic Translation
Convert energy model objects into airflow model objects
Process is 100% automatic
1
3
2
4
1
2
3
4

## Slide 18: Applications
Infiltration calculation (presently a part of RMT)
HVAC security modeling (described in ASHRAE paper)
IAQ/IEQ building performance assessment
…

## Slide 19: Summary on Airflow
Enable enhanced energy modeling with airflow modeling
CONTAM objects are integrated into OpenStudio (as of version 1.1.3)
Current applications include infiltration and security modeling

## Slide 20: Modeling Theory
Reduce Complexity
Detailed
Reduced Order Model
Simplified Thermal Zones
Simplified Geometry
Run Time
9 min
5 min
2 min
15 min
Energy Models

## Slide 21: OpenStudio/E+
SUBSTANTIAL
Data
Flow
Energy Simulation
Building101
Validation Case Studies
One Montgomery
Healthcare/Lab Case Study
tools.eebhub.org/game
User Input
Geometry
Building Component Library (BCL)
Enclosure
Typical Room
Mechanical
Lighting
Schedules
Interactive Output
Tracking Sheet
Building Component Library (BCL)
Energy End-Use
Financial
Measure Selection

## Slide 22: Retrofit Decisions & Features
Factors that impact retrofit decisions:
Building Type, Size, Location, Age
Financial constraints (capital availability, financial return requirements)
Measure cost & performance uncertainty
Building use, reliability, and disruption constraints
Planned capital projects and maintenance
Energy source uncertainty (price, availability)
Technological change (new technology, regulation of old technology)
Environmental considerations (greenhouse gas emissions, water use)
Indoor environmental quality and productivity impacts
Features for January:
Add new measures (Economizer, service hot water, exterior lighting)
Features for March:
  ASHRAE Standard 90.1 HVAC Systems (No3- No8)
Schedule editor
Upload measures to the Building Component Library
  Benchmark building with the LEED NC buildings
Editable measure information and cost assumptions
Editable financial assumptions & financial planning tab
Acknowledgements:
PSU: Jin Bin Li, Mujing Wang, Nicholas Mattise, Josh Kuiros, Yang-Seon Kim, Ibrahim Alanqar, and Liusheng Yan
NREL: Kyle Benne, Andrew Parker, Nick Long, Brent Griffith, and Larry Brackney

## Slide 23
Measure Name | Description
Occupancy/Schedule | 
Heating Set Back | Set back the thermostat heating setpoint from 21°C(70°F) to 13°C(55°F) when unoccupied
Cooling Set Back | Set back the thermostat cooling setpoint from 24°C(75°F) to 32°C(90°F) when unoccupied
Ventilation Set Back | Turn off building ventilation when unoccupied
Plug Load | 
EnergyStar Equipment | Require that new office equipment be EnergyStar certified, assuming a 15% reduction in equipment power density
Plug Load Control | During unoccupied hours, reduce plug load to 60% of prior unoccupied equipment power density
Lighting | 
Occupancy-Based Lighting Sensors | During unoccupied hours, reduce lighting power to 80% of prior unoccupied lighting power density
Daylight-Based Dimming | Change lighting schedule to dim lighting to target lighting level when daylight available
Office Lamp/Ballast Retrofit | Replace lamps and ballasts in all office fixtures to T8 with low ballast factor
Luminaire Retrofit | Convert lighting system to 90% of ASHRAE 90.1 Lighting Power Density values
Enclosure | 
Increase Roof Insulation by R-10 | Add R-20 insulation to roof
Increase Wall Insulation by R-10 | Add R-10 insulation to exterior walls
Increase Wall Insulation by R-20 | Add R-20 insulation to exterior walls
Window Upgrade | Replace windows with low-e, double pane, argon fill windows
Window Film | Install a reflective window coating to lower solar heat gain
Door Weatherization | Weatherstrip doors to reduce infiltration by 5%
Exterior Wall Weatherization | Air seal exterior wall to reduce infiltration by 15%
HVAC | 
Outdoor Air Economizer | Install an outdoor-air economizer for the venilation system
Condensing Boiler | Install a condensing boiler with 95% efficiency at 120°F return temperature
Condensing Unit Replacement | Replace condensing units with 30% higher efficiency units
RMT Measures